## Planilha1
CALCULATION OF PIN POLLUTION LEVEL 15kv
Data input
Side Measure |  | 19 | cm | Approximate measurement area
Lower edge measure |  | 5 | cm | Side area |  | 613 | cm^2
Lower center measurement |  | 4.5 | cm | Lower area |  | 149 | cm^2
Greater circumstance |  | 32 | cm | Total area |  | 762 | cm^2
Smaller circumstance |  | 22 | cm | Measuring water |  | 300 | ml
|  |  | sigma/cm | g/l | sigma/m | g | g | mg/cm^2 | mg/cm^2
|  |  | Used Values |  | Measured values |  |  | Output
|  | Sample | Solution | Kaolin mass | sigma | wi | wf | ESDD | NSDD | Sa
| 1 Extraction | 1 | 60 | 16 | 0.0909 | 2.2124 | 2.9966 | 0.2 | 1.0291 | 0.50801
|  | 2 | 60 | 16 | 0.1109 | 2.0937 | 3.4968 | 0.24547 | 1.8413 | 0.62349
|  | 3 | 60 | 16 | 0.1205 | 2.4284 | 4.297 | 0.26738 | 2.4522 | 0.67915
|  | 4 | 60 | 16 | 0.0927 | 2.4108 | 3.4635 | 0.20408 | 1.3815 | 0.51837
|  | 5 | 60 | 16 | 0.0831 | 2.1102 | 2.9463 | 0.18235 | 1.0972 | 0.46317
| 2 Extraction | 1 | 40 | 8 | 0.0621 | 2.4002 | 3.2225 | 0.13508 | 1.0791 | 0.34311
|  | 2 | 40 | 8 | 0.0618 | 2.4148 | 3.0331 | 0.13441 | 0.81142 | 0.3414
|  | 3 | 40 | 8 | 0.0508 | 2.2138 | 2.8028 | 0.10984 | 0.77297 | 0.27899
|  | 4 | 40 | 8 | 0.0473 | 2.1505 | 2.5635 | 0.10205 | 0.54199 | 0.25921
|  | 5 | 40 | 8 | 0.0585 | 2.234 | 2.5421 | 0.12702 | 0.40433 | 0.32264
| 3 Extraction | 1 | - | 16 | 0.003 | 2.1958 | 4.1909 | 0.0059587 | 2.6182 | 0.015135
|  | 2 | - | 16 | 0.00494 | 2.1231 | 3.6535 | 0.0099599 | 2.0084 | 0.025298
|  | 3 | - | 16 | 0.00153 | 2.2504 | 3.5193 | 0.0029782 | 1.6652 | 0.0075646
|  | 4 | - | 16 | 0.002 | 2.252 | 3.653 | 0.0039244 | 1.8386 | 0.0099681
|  | 5 | - | 16 | 0.00107 | 2.1226 | 2.954 | 0.0020605 | 1.0911 | 0.0052338
| 4 Extraction | 1 | - | 8 | 0.00133 | 2.1336 | 3.279 | 0.002578 | 1.5031 | 0.0065481
|  | 2 | - | 8 | 0.00178 | 2.3906 | 3.1417 | 0.0034806 | 0.9857 | 0.0088406
|  | 3 | - | 8 | 0.00105 | 2.2201 | 2.82 | 0.0020209 | 0.78727 | 0.0051331
|  | 4 | - | 8 | 0.00082 | 2.2239 | 2.6755 | 0.0015666 | 0.59265 | 0.003979
|  | 5 | - | 8 | 0.00064 | 2.4242 | 2.7234 | 0.0012136 | 0.39265 | 0.0030826
| 5 Extraction | 1 | - | 20 | 0.00158 | 2.1921 | 4.2015 | 0.0030785 | 2.637 | 0.0078193
|  | 2 | - | 20 | 0.0013 | 2.1428 | 3.7722 | 0.0025181 | 2.1383 | 0.0063961
|  | 3 | - | 20 | 0.00125 | 2.0885 | 3.7227 | 0.0024184 | 2.1446 | 0.0061428
|  | 4 | - | 20 | 0.00116 | 2.3609 | 3.7936 | 0.0022393 | 1.8802 | 0.0056878
|  | 5 | - | 20 | 0.00086 | 2.3854 | 3.58 | 0.0016453 | 1.5677 | 0.0041791
| 6 Extraction | 1 | - | 10 | 0.00095 | 2.1967 | 3.4831 | 0.0018229 | 1.6882 | 0.0046303
|  | 2 | - | 10 | 0.00096 | 2.2043 | 3.304 | 0.0018427 | 1.4432 | 0.0046805
|  | 3 | - | 10 | 0.00076 | 2.1724 | 2.8642 | 0.0014486 | 0.90787 | 0.0036795
|  | 4 | - | 10 | 0.00056 | 2.0877 | 2.8359 | 0.0010577 | 0.98189 | 0.0026865
|  | 5 | - | 10 | 0.00057 | 2.1327 | 2.6151 | 0.0010771 | 0.63307 | 0.0027359
| 7 Extraction | 1 | - | 6 | 0.00075 | 2.1161 | 2.7777 | 0.001429 | 0.86824 | 0.0036296
|  | 2 | - | 6 | 0.00085 | 2.1616 | 2.7523 | 0.0016256 | 0.7752 | 0.0041291
|  | 3 | - | 6 | 0.00887 | 2.2261 | 2.6489 | 0.0182 | 0.55486 | 0.046229
|  | 4 | - | 6 | 0.0131 | 2.2049 | 2.5298 | 0.027196 | 0.42638 | 0.069078
|  | 5 | - | 6 | 0.013 | 2.1206 | 2.4078 | 0.026982 | 0.3769 | 0.068535
| 8 Extraction | 1 | - | 25 | 0.01067 | 2.4018 | 4.157 | 0.022015 | 2.3034 | 0.055919
|  | 2 | - | 25 | 0.01063 | 2.1446 | 4.0576 | 0.02193 | 2.5105 | 0.055703
|  | 3 | - | 25 | 0.01064 | 2.461 | 4.4851 | 0.021952 | 2.6563 | 0.055757
|  | 4 | - | 25 | 0.01045 | 2.2659 | 3.9556 | 0.021548 | 2.2175 | 0.054732
|  | 5 | - | 25 | 0.01035 | 2.162 | 3.4274 | 0.021336 | 1.6606 | 0.054193